## Slide 1: Fire Safety for New Battery Technologies What's in Store for Your Jurisdiction?
Kelly Nicolello
Senior Regulatory Engineer
Notes: For several decades there weren’t many advancements in electrical power systems that directly impacted the fire service. Certainly saw new technologies introduced, primarily of interest to electrical inspectors. More recently the introduction of renewable energy systems, and on site storage and power generation introduced, along with benefits, some fire safety challenges for the fire service. Energy systems, in particular ESS are a rapidly evolving issue that is creating some significant safety challenges.

## Slide 2: Energy Storage System (ESS) Applications
Facility emergency and standby power
Uninterruptable power supplies
Telecommunication system continuity
Web oriented data centers
Historical stationary battery system applications
Notes: In February 2013, the California Public Utilities Commission (CPUC) determined that Southern California Edison must procure 50 MW of energy storage capacity by 2021 in Los Angeles area. Other States are looking to the example that California is setting, and Congress has introduced two bills that establish incentives for storage deployment.
The bills before congress are S. 1030 (STORAGE Act ) and S. 795 (MLP Parity Act). Details on the California bill (AB 2514) can be found on the CPUC website: http://www.cpuc.ca.gov/PUC/energy/electric/storage.htm

## Slide 3: Energy Storage System (ESS) Applications
Expanding energy storage infrastructure
Grid balancing and resiliency
Load shedding
Mitigating renewable energy intermittency
“Smart meter” cost savings
Commercial and residential applications
Evolving stationary battery system applications
Notes: In February 2013, the California Public Utilities Commission (CPUC) determined that Southern California Edison must procure 50 MW of energy storage capacity by 2021 in Los Angeles area. Other States are looking to the example that California is setting, and Congress has introduced two bills that establish incentives for storage deployment.
The bills before congress are S. 1030 (STORAGE Act ) and S. 795 (MLP Parity Act). Details on the California bill (AB 2514) can be found on the CPUC website: http://www.cpuc.ca.gov/PUC/energy/electric/storage.htm

## Slide 4: Historical Stationary Battery Systems
Primarily lead acid battery systems
Hazards include:
Corrosive liquids
Hydrogen off gassing
Electrical energy considerations
Notes: In February 2013, the California Public Utilities Commission (CPUC) determined that Southern California Edison must procure 50 MW of energy storage capacity by 2021 in Los Angeles area. Other States are looking to the example that California is setting, and Congress has introduced two bills that establish incentives for storage deployment.
The bills before congress are S. 1030 (STORAGE Act ) and S. 795 (MLP Parity Act). Details on the California bill (AB 2514) can be found on the CPUC website: http://www.cpuc.ca.gov/PUC/energy/electric/storage.htm

## Slide 5: Modern Battery Technologies
Stationary battery technologies include
Flow batteries
Sodium-sulfur batteries
Lithium-ion batteries
Others technologies on the way
Energy density and cost drive new battery technologies

## Slide 6: Flow Batteries
Two tanks of liquids, pumped past a membrane between electrodes
Electric current produced while both liquids circulate in their own respective space
System includes pumps, sensors, control units, secondary containment
Will fire and emergency services have a plan for responding to incidents?

## Slide 7: Sodium–Sulfur Batteries
High energy density, and long cycle life
Operating temperatures of 300 to 350 °C
Sodium polysulfides are highly corrosive
Vacuum insulated boxes protect sodium from water and oxidizing atmospheres
Pure sodium spontaneously burns in contact with air and moisture

## Slide 8: Lithium-ion Batteries
Excellent energy density
The current battery of choice
Batteries and systems are readily available

## Slide 9: Li-ion Battery Safety Considerations
Overheating and cell rupture is possible from:
Overcharging
Short circuits
Manufacturing defects
Thermal runaway in one battery will readily spread to adjacent cells

## Slide 10: Li-ion Batteries – Abnormal Charging

## Slide 11: Fire Code Battery System Requirements
Since 1997 (lead-acid) battery systems allowed in incidental use areas
1 or 2 hour fire-rated separations
Hazmat requirements exempted
Spill control, ventilation, smoke detection
Battery quantities unlimited
Location in building not regulated
Standby & emergency power, UPS use
Current codes do not adequately protect newer battery technologies

## Slide 12: Addressing New Potential Hazards
How can you address ESS hazards not covered by the code?
Large quantities of Lithium-ion batteries
New battery and other ESS technologies
Proven effective protection methods not yet available
Concern - New ESS technologies and applications are arriving before code requirements can address potential hazards
What do fire and emergency services need to know to respond to incidents

## Slide 13: Proposed Battery System Requirements
NFPA 1 TC approved new battery system requirements
Proposal F95-16 for the IFC/IBC and RB171-16 for the IRC were approved at ICC Public Comment Hearings
Intent - Both 2018 fire codes will include similar requirements
NFPA 855 TC recently formed to develop an ESS standard

## Slide 14: Considerations behind the IFC Code Proposals
Section 608 addresses lead acid battery system hazards
Covers lithium batteries but doesn’t effectively address associated hazards
Does not regulate other battery technologies – outside of scope of Section 608
Societal needs for ESS installations
Recognition that additional research, large scale testing and standards are needed to address unknowns

## Slide 15: Concepts for Protecting Energy Systems NFPA 550: Guide to the Fire Safety Concepts Tree
Listed batteries and equipment
BMS and compatible equipment
Proper installation
Ventilation, as needed
Fire-resistive separation
Suppression and control
Array spacing and MAQs
Location in building or on property
Signage

## Slide 16: IFC Proposal - Threshold Limits
Current threshold
50 gallons electrolyte for lead-acid, Ni-Cad, VRLA
1,000 pounds for lithium-ion and lithium metal polymer
Other technologies not covered
Use - Standby and emergency power or UPS
2018 threshold
Lead acid, Ni-Cad - 70 KWh
Lithium, sodium all types - 20 KWh
Flow batteries - 20 KWh
Other battery technologies 10 KWh
Use - No limitations

## Slide 17: 2018 IFC – General
Installation permits
Construction documents
Hazard mitigation analysis (HMA) shall be provided for:
Battery technologies not specifically covered
Multiple battery technologies in a room with a potential for adverse interactions
3. When allowed as a basis for increasing MAQs

## Slide 18: 2018 IFC – General
The HMA will evaluate the consequences of failure modes
Thermal runaway in a single battery array
Failure of the energy management system
Failure of ventilation system
Voltage surges on the primary
Short circuits on the load side of the batteries
Failure of the smoke or gas detection, fire suppression
The fire code official is authorized to approve the hazardous mitigation analysis based on the HMA.
The HMA is a tool to address unknowns with new technologies

## Slide 19: 2018 IFC – General
Seismic and structural design per IBC Chapter 16
Vehicle impact protection
Combustible storage not allowed in battery rooms, cabinets Testing, maintenance and repairs per the manufacturer’s instructions

## Slide 20: Location and Construction
2018 IFC
Battery room floor < 75 feet above the lowest level of fire department vehicle access, and < 30 feet below the lowest level of exit discharge Exception: Installations on noncombustible rooftops > 75 feet that do not obstruct fire department rooftop operations when approved by the fire code official.
Current IFC
No restrictions on location in a building or on the property

## Slide 21: Fire-Resistive Separations
2018 IFC
No changes, still allowed in incidental use areas
Current IFC
Battery room must be separated from other areas of the building in accordance with Section 509.1 of the International Building (1 or 2 hours depending on adjacent occupancy)

## Slide 22: New Stationary Storage Battery Concepts
Pre-packaged stationary storage battery system
Pre-engineered stationary storage battery system

## Slide 23: Battery Arrangements
IFC 2018
Storage batteries, prepackaged , and pre-engineered battery systems must be segregated into arrays not exceeding 50 KWh each
Each battery array must be spaced three feet from other stationary battery arrays and from walls in the storage room
    Exceptions:
    1.Lead acid batteries arrays
    2. Listed pre-engineered and prepackaged battery systems may be 250 KWh
Current IFC
No restrictions on battery arrangements within the room

## Slide 24: New Battery Array Concepts
Max. 50 KWh each
Max. 250 KWh each for listed systems
Spaced min. 3 ft. from other arrays and from walls
Other arrangements as approved by AHJ based on large scale fire and fault condition testing

## Slide 25: Maximum Allowable Quantities
2018 IFC
MAQ for an incidental use area within buildings is 600 KWh
100 KWh for technologies not covered by the code
No limit for lead acid battery systems
Fire areas containing battery systems above the MAQ shall comply with Group H requirements
Exception: When approved, larger quantities allowed based on HMA and large scale fire and fault condition testing by an approved testing laboratory.
Current IFC
No restrictions on the quantity of batteries in an incidental use area

## Slide 26: 2018 IFC - Outdoor Installations
Installations in outdoor enclosures or containers which can be occupied are treated as battery storage rooms
Exception: Battery arrays in noncombustible containers are not required to be spaced three feet from the container walls.
Outdoor battery systems must be separated 5 feet from lot lines, public ways, buildings and other exposure hazards

## Slide 27: 2018 IFC Batteries and Equipment
Storage batteries (except lead-acid) must be UL 1973 listed
Prepackaged/pre-engineered systems must be UL 9540 listed
Battery chargers must be listed and compatible with the battery chemistry and the manufacturer's charging specifications
Inverters must be listed and suitable for utility interactive system use if operating in parallel with the electrical grid
Vented batteries must include flame-arresting safety caps

## Slide 28: 2018 IFC - Battery {Energy} Management Systems
An approved BMS must be provided to monitor and balance cell voltages, currents and temperatures within the manufacturer's specifications.
The BMS must transmit an alarm to an approved location if hazardous temperatures or other conditions such as short circuits, overvoltage or undervoltage are detected.

## Slide 29: Battery Room Protection
Automatic smoke detection system per Section 907.2.
Signage on or near battery room doors:
Cautionary markings to identify hazards with specific batteries (corrosives, water reactive, hydrogen gas, Li-ion batteries, etc.)

## Slide 30: 2018 IFC - Battery Specific Protection
Systems that release toxic/highly toxic gases during charging, discharging and normal use must comply with Chapter 60
Exhaust ventilation is required for system that produce combustible gases during normal use
Spill control and neutralization required for systems with liquid electrolytes

## Slide 31: Fire Suppression Systems
2018 IFC
Battery rooms need a NFPA 13 system
Commodity classifications per Chapter 5 of NFPA 13.
If the storage batteries are not addressed in Chapter
5 of NFPA 13, the fire official can approve the system based on full scale fire and fault condition testing
Current IFC
Not required

## Slide 32: Fire Suppression Systems - Discussion
How to protect battery rooms and exposures if no sprinklers are listed for use with battery systems?
Hilden Germany Warehouse Fire
32 tons of cylindrical Li-ion batteries were reportedly involved
600 KWh of Li-ion batteries (MAQ) in an incidental use area ~ 7 tons

## Slide 33: Research Needed to Resolve Uncertainties
Notes: Building and Fire Codes may also require updates

## Slide 34: Large Scale Fire Testing Needed for Evaluate Battery Array Arrangements

## Slide 35: New IFC Chapter 12 – Energy Systems
Consolidates new and existing energy related requirements
1201-02 General and definitions
1203 Emergency and standby power systems
1204 Solar photovoltaic power systems
1205 Fuel cell energy systems (New)
1206 Electrical energy storage systems
  1206.1 Scope
  1206.2 Stationary storage battery systems
  1206.3 Electrical capacitor energy systems (New)

## Slide 36: Consumer Considerations
The “Smart grid” enables consumers to enhance their electric utilization with consumer storage systems
Notes: The deployment of EV’s is another form of customer storage of electricity, this is permitted where installed to comply with NEC Section 625.48.
Increasingly, deployment of new ESS technologies on the customer side of the meter is changing the electrical nature of customer requirements. The evolution of the “smart grid” is enabling customers to shape their requirements to improve their own utilization of electricity, while also contributing to improved grid reliability and performance. These developments create an opportunity for customer storage to play an increasing role in grid services.
ESS’s should not be confused with UPS systems. A UPS is used to provide alternating-current power to a load for some period of time in the event of a utility power failure. In addition, it may provide a more constant voltage and frequency supply to the load, reducing the effects of utility voltage and frequency variations. In the development of UL 1778, it was not anticipated to be for continuous use in the applications where an energy storage systems are intended to be used.

## Slide 37: Residential ESS
Li-ion Battery System
Utility Interactive Inverter
Electrical Panel
Electric Vehicle
Solar or off-peak demand utility power charges the battery system

## Slide 38: Residential Storage Battery Systems
Lithium-ion with BMS
One manufacturer has 6.4 KWh unit ~$3000
Will provide power for a typical home overnight, but probably not A/C
Multiple systems can be provided to increase capacity

## Slide 39: 2018 IRC Battery Systems (RB171-16)
Applies to battery systems > 1KWh
Battery systems must be listed to UL 9540
Installed per the manufacturer's instructions
Cannot be installed within habitable space of a dwelling unit
Electrical installation same as residential PV systems
Ventilation required if charging produces hydrogen gas
Vehicle impact protection, if applicable

## Slide 40: Repurposing EV Battery Systems
Used Li-ion EV battery systems that no longer provide a sufficient driving range will be replaced in the vehicle, but still retain significant capacity that may be used in non-EV applications
These batteries can be used to capture surplus renewable energy during times
of low demand for use during higher demand time periods.
UL 1974 being developed to verify safety methodology

## Slide 41: 2018 IRC Battery System Reqiurements Repurposed Batteries
Where approved, repurposed unlisted battery systems from electric vehicles are allowed to be installed outdoors or in detached sheds ≥ five feet from exterior walls, property lines and public ways.

## Slide 42: Take Aways – Modern Battery Storage Systems
What do code authorities need to know?
Resiliency and cost savings are driving demand for new energy solutions
Installations may be coming to your jurisdiction soon
Hazards associated with various energy technologies
Prudent to share information with administrators, faculty and emergency responders
New code requirements cover traditional, new and future technologies

## Slide 43: Discussion